## Summary of Cost
Consolidated Summary of the Proposed Drinking Water Supply Schemes for Bata Tal,Peshawar, KPK
SUMMARY OF COST
S.NO. | DESCRIPTIONS | No's | BOQ Amount (Rs) | Total Amount (Rs)
1 | Solarization of submersible pump | 1
2 | Pressurized water distribution network | 1
3 | Rehabilitation of Borehole | 1
4 | Rehabilitation of Pump Room 10' x 10' | 1
SUB-TOTAL ( 1+2+3+4): Rs
5 | Provisional Sum Item (PSI): This item is designated as a Provisional Sum in accordance with the Conditions of Contract, to cover works that cannot be fully quantified or defined at the time of site assessment due to uncertain site conditions. The Contractor shall include an amount equivalent to 2% of the total cost of Item No. 1 to 4 and, to be utilized as directed by the Engineer.
TOTAL COST Rs.
TOTAL COST Rs. (M)

## 1.Abstract Solarization
BOQ
Solarization of Submersible Pump For Proposed Drinking Water Supply Schemes for Bata Tal, Peshawar ,KPK
Abstract Of Cost
Item | MRS 2025 (B) | Description | Unit | Qty | Unit Rate | Total Amount
Solarization of Submersible Pumping System
1 | 26-01-d-01 | Solar PV Modules Supply, installation, testing, and commissioning of Mono-crystalline A-Grade Solar PV Modules, rated per watt, complete in all respects, in accordance with approved technical specifications and as directed by the Engineer. | Watt | 35960
2 | 15-02-b-05 | PVC Conduit Pipe (1.5” I/D) – Open Wiring Providing, supplying, and installing heavy-duty PVC conduit pipe (40mm dia), recessed in walls, including all accessories, bends, couplers, and finishing, conforming to IEC 61386." | Rft | 348
3 | 26-01-b-02 | PVC Flexible Pipe (1.5") Supply and installation of PVC flexible pipe (1.5" internal diameter), including all necessary fittings, jointing, and accessories, complete in all respects as per approved drawings and specifications. | Rft | 232
4 | NSI | "Copper Thimbles & Ferrules Providing, supplying, and installation of high-quality Copper thimbles & ferrules(cable lugs), manufactured from electrolytic grade copper, suitable for termination of electrical cables, complete with proper crimping and fixing. The thimbles shall be tinned for corrosion resistance, ensuring high conductivity, durability, and secure cable connections. Suitable for specified cable sizes and conforming to relevant IEC standards. Complete in all respects as per specifications and as directed by the Engineer" | Job | 1
5 | NSI | Protection, Control and Monitoring Components for 30 kW Solar VFD Supply, installation, testing, and commissioning of complete protection, control, and monitoring system for 30 kW solar pump VFD, including MC4 connectors; 4th generation 3-in-1 voltage protection device with integrated kWh meter (or equivalent approved); 4-pole AC circuit breakers for utility (WAPDA) input, light load, and heavy load circuits; changeover switch/breaker ; double-pole DC circuit breaker for PV string(s); AC and DC surge protection devices; including all interconnections, terminations, mounting, and accessories, complete in all respects as per approved specifications and as directed by the Engineer. | Job | 1
6 | NSI | DB Box for 30 kW VFD Inverter (16 Gauge) Supply, installation, testing, and commissioning of distribution board (DB) box for 30 kW VFD inverter, fabricated from 16-gauge mild steel sheet, powder-coated, dust and weather-resistant, suitable for indoor/outdoor installation; complete with proper mounting arrangement, busbars, earthing, cable glands, and all necessary accessories, in accordance with approved drawings and specifications, and as directed by the Engineer. | Job | 1
7 | NSI | PVC Distribution Board (12-Way) for AC/DC Breakers Supply and installation of 12-way PVC distribution board, suitable for accommodating AC and DC breakers, fabricated from high-quality, flame-retardant PVC, complete with internal busbars, DIN rail, neutral and earth terminals, front cover, and all necessary accessories; including fixing, wiring, and terminations, complete in all respects in accordance with approved specifications and as directed by the Engineer. | Job | 2
8 | NSI | DC Copper Cable (1×10 sq.mm, CU/PVC/PVC) Supply, installation, laying, termination, testing, and commissioning of 1-core 10 sq.mm copper cable (CU/PVC/PVC insulated), including all accessories such as lugs, glands, insulation, and proper routing, complete in all respects in accordance with approved specifications and as directed by the Engineer. | Rft | 1392
9 | 15-06-f | Sub-Main Wiring (7/0.064 Cable) Providing, supplying, and installation of single-core PVC insulated and sheathed copper conductor cable (7/0.036”), from distribution board to switchboards/power outlets, conforming to IEC 60227/60502. | Rft | 300
10 | 26-01-h-01 | MC4 Connectors Supply and installation of MC4 connectors (TÜV approved), suitable for solar PV systems, complete with proper connections and weatherproofing | Pair | 10
11 | 26-01-i-04 | Solar Pump Inverter (30 kW) Supply, installation, testing, and commissioning of 3-phase (380V) Solar Pump Inverter (MPPT-based VFD), 30 kW, including all protections, control systems, and accessories, as per approved specifications. | No | 1
12 | NSI | Adjustable Steel Mounting Structure for Solar Panels Supply, fabrication, primer coating with red oxide, painting (two coats), and erection of an adjustable steel mounting structure for solar panels, complete in all respects as per approved drawings, specifications, and as directed by the Engineer. The structure shall comprise two integrated components: Primary Support Structure: Fabricated using a steel girder (H-section) of size 7" × 3", with adjustable height ranging from 5 ft to 10 ft, as per site requirements or as directed by the Engineer. Secondary Panel Mounting Frame: Designed to support solar panels as per detailed drawings (Annex-VII), fabricated using 1.5" × 3" pipes, 1.5" × 1.5" pipes (for bracing/lever), 3" diameter circular pipe, 1" × 2" pipes, and gusset plates. The scope includes cutting, welding, drilling, assembly, installation, and provision for tilt-angle adjustment, ensuring structural stability and durability under site conditions. All materials and workmanship shall conform to approved specifications. | Nos | 58
13 | NSI | Earthing System for Inverter and Steel Structure Supply, installation, testing, and commissioning of a complete earthing system for inverter and solar mounting steel structure, comprising independent earthing points for each system, with a minimum spacing of 8 ft between earth pits, complete in all respects as per specifications and as directed by the Engineer. Each earthing point shall consist of a bore of minimum 10 ft depth and 3" diameter, incorporating a 2" diameter GI pipe installed vertically. A 16 mm diameter copper rod shall be inserted inside the GI pipe, surrounded by layers of charcoal and salt to enhance conductivity. The copper rod shall be connected using 12-gauge copper wire with appropriate copper U-clamps. The earthing conductors shall be routed separately, with independent connections provided to the solar steel mounting structure and the inverter, ensuring effective grounding and system protection. All materials, installation, and workmanship shall conform to approved specifications or as per the Engineer instruction | No | 2
14 | 26-01-n-03 | SS Nuts & Bolts Supply and installation of stainless steel nuts, bolts, washers, and fasteners, of approved quality, complete in all respects for proper assembly of the system. | Watt | 35960
15 | 24-91-g | Submersible Pump (30 HP) Supply, installation, testing, and commissioning of submersible pump set (ISO 9906 certified), coupled with rewindable electric motor with AC winding, having discharge capacity greater than 3000 IGPH and output capacity between 20–30 WHP (30 HP), complete in all respects as per approved technical specifications. | WHP | 30
16 | 24-50-c-02 | Submersible Flat Cable (3×16 sq.mm) Supply and installation of submersible flat cable (3-core × 16 sq.mm), made of 99.9% copper conductor with double PVC insulation, conforming to relevant BSS/IEC standards, including all terminations and accessories. | M | 110
Grand Total Cost in PKR
Pressurized Water Distribution Network
17 | NSI | HDPE Pipeline (25 mm dia, PN-10) (0.98") Providing, laying, cutting, jointing, testing, and disinfection of High-Density Polyethylene (HDPE) pipe conforming to DIN 8074/8075 / ISO 4427, laid in trenches, including all fittings and accessories, complete in all respects as per specifications, excluding excavation. | Rft | 500
18 | NSI | HDPE Pipeline (50 mm dia, PN-10) (1.96") Providing, laying, cutting, jointing, testing, and disinfection of HDPE pipe conforming to DIN 8074/8075 / ISO 4427, complete in all respects as per specifications, excluding excavation. | Rft | 500
19 | NSI | HDPE Pipeline (75 mm dia, PN-10) (2.95") Providing, laying, cutting, jointing, testing, and disinfection of HDPE pipe conforming to DIN 8074/8075 / ISO 4427, complete in all respects as per specifications, excluding excavation. | Rft | 500
20 | NSI | HDPE Pipeline (90 mm dia, PN-10) (3.54") Providing, laying, cutting, jointing, testing, and disinfection of HDPE pipe conforming to DIN 8074/8075 / ISO 4427, complete in all respects as per specifications, excluding excavation. | Rft | 300
21 | NSI | HDPE Pipeline (110 mm dia, PN-10) (4.33") Providing, laying, cutting, jointing, testing, and disinfection of HDPE pipe conforming to DIN 8074/8075 / ISO 4427, complete in all respects as per specifications, excluding excavation | Rft | 300
22 | 24-22-a-03 | Sluice Valve (3" dia, PN-16) (76.2mm) Providing and installation of sluice valve (75 mm dia) suitable for GI, PVC, MS, and HDPE pipelines, including rubber sheet, jointing materials, and all accessories, complete in all respects. | Each | 4
23 | 24-22-b-03 | Sluice Valve (4" dia, PN-16) (101.6mm) Providing and installing a sluice valve (100 mm dia) suitable for all types of pipelines, including all jointing materials and accessories, complete in all respects. | Each | 4
24 | 24-30-f-02 | HDPE Tee (25 mm dia) (0.98") Providing and installation of HDPE tee (25 mm dia), including jointing and accessories, complete in all respects. | Each | 2
25 | 24-30-f-05 | HDPE Tee (50 mm dia) (1.96") Providing and installation of HDPE tee (50 mm dia), complete in all respects. | Each | 2
26 | 24-30-f-07 | HDPE Tee (75 mm dia) (2.95") Providing and installation of HDPE tee (75 mm dia), complete in all respects. | Each | 2
27 | 24-30-f-08 | HDPE Tee (90 mm dia) (3.54") Providing and installation of HDPE tee (90 mm dia), complete in all respects. | Each | 2
28 | 24-30-f-09 | HDPE Tee (110 mm dia) (4.33") Providing and installation of HDPE tee (110 mm dia), complete in all respects. | Each | 2
29 | 24-30-g-02 | HDPE Bend (25 mm dia) (0.98") Providing and installation of HDPE bend (25 mm dia), complete in all respects | Each | 2
30 | 24-30-g-05 | HDPE Bend (50 mm dia) (1.96") Providing and installation of HDPE bend (50 mm dia), complete in all respects. | Each | 2
31 | 24-30-g-07 | HDPE Bend (75 mm dia) (2.95") Providing and installation of HDPE bend (75mm dia), complete in all respects. | Each | 2
32 | 24-30-g-08 | HDPE Bend (90 mm dia) (3.54") Providing and installation of HDPE bend (90 mm dia), complete in all respects. | Each | 2
33 | 24-30-g-09 | HDPE Bend (110 mm dia) (4.33") Providing and installation of HDPE bend (110 mm dia), complete in all respects. | Each | 2
34 | 24-30-h-02 | HDPE Adaptor (25 mm dia) (0.98") Providing and installation of HDPE adaptor (25 mm dia), complete in all respects. | Each | 2
35 | 24-30-h-05 | HDPE Adaptor (50 mm dia) (1.96") Providing and installation of HDPE adaptor (50 mm dia), complete in all respects. | Each | 2
36 | 24-30-h-07 | HDPE Adaptor (75 mm dia) (2.95") Providing and installation of HDPE adaptor (75 mm dia), complete in all respects. | Each | 2
37 | 24-30-h-08 | HDPE Adaptor (90 mm dia) (3.54") Providing and installation of HDPE adaptor (90 mm dia), complete in all respects. | Each | 2
38 | 24-30-h-09 | HDPE Adaptor (110 mm dia) (4.33") Providing and installation of HDPE adaptor (110 mm dia), complete in all respects. | Each | 2
39 | NSI | HDPE Compression Coupler (75 mm dia) (2.95") Providing and installation of HDPE compression coupler (75 mm dia), complete in all respects. | Each | 2
40 | NSI | HDPE Compression Coupler (90 mm dia) (3.54") Providing and installation of HDPE compression coupler (90 mm dia), complete in all respects. | Each | 2
41 | NSI | HDPE Compression Coupler (110 mm dia) (4.33") Providing and installation of HDPE compression coupler (110 mm dia), complete in all respects. | Each | 1
42 | NSI | HDPE Reducer Tee / Coupler (75 mm dia) (2.95") Providing and installation of HDPE reducer tee/coupler (75 mm dia), complete in all respects. | Each | 2
43 | NSI | HDPE Reducer Tee / Coupler (90 mm dia) (3.54") Providing and installation of HDPE reducer tee/coupler (90 mm dia), complete in all respects. | Each | 2
44 | NSI | HDPE Reducer Tee / Coupler (110 mm dia) (4.33") Providing and installation of HDPE reducer tee/coupler (110 mm dia), complete in all respects. | Each | 1
45 | NSI | HDPE Clamp Saddle (75 mm dia) (2.95") Providing and installation of HDPE clamp saddle (75 mm dia), complete in all respects. | Each | 2
46 | NSI | HDPE Clamp Saddle (90 mm dia) (3.54") Providing and installing the HDPE clamp saddle (90 mm dia), complete in all respects. | Each | 2
47 | NSI | HDPE Clamp Saddle (110 mm dia) (4.33") Providing and installation of HDPE clamp saddle (110 mm dia), complete in all respects. | Each | 1
48 | NSI | Excavation of Trenches Excavation of trenches (1.25 ft width, up to 2.5 ft depth) by manual or mechanical means for pipeline laying, including backfilling, compaction, and restoration of site, complete in all respects. | cft | 6250
49 | 06-05-f | Plain Cement Concrete (One Part of Cement, Two Parts of Sand & Four Parts of Crush) In-situ mixing, placing, compaction, finishing, and curing of plain cement concrete (One Part of Cement, Two Parts of green & free from clay lumps Sand, and Four Parts of blasted crushed aggregate ) in 4" over the excavted trench or as where applicable, including provision of all materials, labor, plant, and equipment, complete in all respects in accordance with specifications and Engineer’s instructions." | cft | 315
50 | NSI | Sand Bedding (6" Thick) Providing and laying 6-inch thick sand bedding in the trench, properly leveled, moistened, and compacted around the pipeline, complete in all respects. | cft | 1725
51 | NSI | Thrust Blocks Construction of concrete thrust blocks at bends, tees, valves, and other required locations, as directed by the Engineer, is complete in all respects. | LS | 1
52 | NSI | House Connections Providing and installing house connections with pipes, fittings, and accessories of appropriate size and length, as per site conditions and as directed by the Engineer, complete in all respects. | Each | 50
Grand Total Cost in PKR

## 2. Abstract Rehabilitation of B
BOQ
Rehabilitation of Borehole at Bata Taal, Peshawar , KPK
Abstract Of Cost
Item | MRS Reference Code 2025 | Description | Unit | Qty | Unit Rate | Total Amount
Rehabilitation of Exisiting Bore Hole (Depth: 400 ft)
1 | 24-13-b | Cleaning and Testing of Tubewell Cleaning and testing of tubewell using DNT (Development by Non-stop Pumping) or approved method for 8" dia and above bore, including cleaning, flushing, and test pumping to achieve clear water and required discharge, complete in all respects as per specifications | Hrs | 36
2 | NSI | EXTRACTION OF OLD MACHINERY: Extraction of Old Pumping Machinery including Submersible pump set & motor, cables , G.i pipes and other specials etc. | Job | 1
3 | 24-05 | Water Sampling and Laboratory Testing Collection and submission of a minimum of two water samples from each borehole to an approved laboratory for physical, chemical, and bacteriological analysis, including proper handling, labeling, and submission of certified test reports. | Per Set | 2
4 | NSI | GI column pipe Providing, installing, jointing, and testing of 3-inch diameter GI column pipe (10 ft length) for tube well installation, complete in all respects including welded flanges, rubber seals/packing, nuts, bolts, non-return (check) valve of 3-inch diameter, clamps, and all necessary fittings, accessories, and appurtenances, including all contractual obligations and unforeseen items as required for proper completion of the work. | Rft | 350
5 | 24-59-c | Replacement of Sluice Valve (4" dia) for Pumping System The work shall include replacement of existing stainless steel (S.S.) sluice valves connected with the pumping machinery and pumping main, including all required fittings such as flanges, packing sheets, nuts, bolts, and accessories, complete in all respects. The sluice valve shall be of 4" (150 mm) diameter and installed in accordance with approved specifications and as directed by the Engineer. | Each | 1
6 | NSI | Automatic Chlorinator System Providing, installation, testing, and commissioning of automatic digital chlorinator system (or equivalent approved), including chlorine dosing unit, storage containers, accessories, and complete setup for disinfection, in accordance with specifications. | No | 1
7 | 14-28-d | Gun Metal Gate Valve (3" dia) Providing and installation of gun metal gate/peet valve (, screwed type) of approved quality, including jointing materials and fixing, complete in all respects. | No | 2
8 | NSI | Tool Kit for Tubewell Operator Supply of complete tool kit for tubewell operation and maintenance, including all standard tools such as pipe wrenches, dies, pliers, hammer, saw, vice, chisels, and carrying bag, complete in all respects as per specifications. | LS | 1
9 | NSI | INAUGURATION PLAQUE Supply and installation of a project signboard fabricated from stainless steel (SS) sheet, nominal size 24″ × 24″, or as directed by the Engineer-in-Charge, complete in all respects. The work shall include cutting, fabrication, fixing, anchoring, and finishing of the signboard, including all necessary materials, fasteners, tools, labor, and safety measures, in accordance with the drawings and technical specifications. | LS | 1
Grand Total (1 to 15) Cost in PKR

## 3. Rehabilitation of Pump House
BOQ
Construction and Drilling of Borehole at Batta Tal
Abstract Of Cost
Item | KP MRS-2025 | Description | Unit | Qty | Unit Rate | Total Amount
A-Renovation of Pump Chamber (10'x10'x10') (Civil Works)
1 | CH-11: S.no 11-13 | FLOATING COAT BEFORE PLASTER Applying a floating coat of neat cement slurry (1/32" thick) over prepared surfaces prior to plastering to enhance bond, complete in all respects. | Per Sft | 518.25
2 | CH-11: S.no 11-08-c | CEMENT PLASTER (1:3, 20MM THICK) Providing and applying cement plaster in a ratio of (1:3) 20 mm (¾") thick, on new surfaces up to a height of 20 ft, including proper surface preparation. pre-wetted to achieve a saturated surface dry (SSD) condition before application and Curing shall be carried out for a minimum period of three (3) days after application. | Per Sft | 518.25
3 | CH-11: S.no 11-18-a | CEMENT POINTING (STRUCK JOINTS) Executing cement pointing with struck joints in cement sand mortar (1:2) on wall surfaces up to 20 ft height, including preparation and finishing, complete in all respects. | Per Sft | 430
4 | CH-11: S.no 11-20-a | PRIMER UNDER WALL PUTTY & DISTEMPER Apply a primer coat under Wall Putty & distemper on prepared surfaces, including necessary surface preparation, complete in all respects. | Per Sft | 622.25
5 | CH-11: S.no 11-20-b | WALL PUTTY APPLICATION Applying wall putty of 2 mm thickness over plastered surfaces to achieve a smooth and even finish, including surface preparation, complete in all respects. | Per Sft | 622.25
6 | SURFACE-REN N.S.I | RED OXIDE PRIMER Applying red oxide primer coat on prepared surfaces of steel /MS Works in the above scope of work prior to application of synthetic enamel paint of approved quality, including surface preparation and complete in all respects as per specifications and the Engineer’s instructions. | Per Sft | 88
7 | SURFACE-REN N.S.I - | SYNTHETIC ENAMEL PAINT Providing and applying synthetic enamel paint of approved quality and specified color on new or existing surfaces of walls, doors, and windows, to achieve a uniform and even finish, complete in all respects as per specifications and Engineer’s instructions. | Per Sft | 88
8 | CH-13: S.no 13-22-a | EMULSION PAINT(INSIDE WALLS / ROOF SLAB) – FIRST COAT Preparing surfaces and applying the first coat of emulsion paint, including surface preparation and uniform application, complete in all respects. | Per Sft | 622.25
9 | CH-13: S.no 13-25-a | SNOWCEM / WEATHER SHIELD(OUT SIDE) – FIRST COAT Preparing external surfaces and applying the first coat of Snowcem/Weather Shield paint, including cleaning and surface preparation, complete in all respects. | Per Sft | 430
10 | CH-25: S.no 25-40 | STEEL GLAZED WINDOW WITH GLASS Fabricating, and fixing openable steel glazed window panels manufactured from L-section pipe (1½" × 1" × 18 gauge) and T-section pipe (2" × 1" × 18 gauge), including all necessary ironmongery (handles, locks, hinges, etc.), and providing, supplying, cutting, and fixing 5 mm thick plain glass, secured with approved aluminium glazing strips and sealed with silicone sealant to ensure proper fixing, airtightness, and watertightness, including all fittings, accessories, welding, cutting, handling, installation, and finishing, complete in all respects as per specifications and Engineer’s instructions. | Per Sft | 16
11 | CH-25: S.no 25-38 | GI WIRE GAUZE FIXING (SAFETY GRILL & MOSQUITO NET) Providing, fabricating, and fixing GI wire gauze of 24 SWG (12 × 12 mesh per sq. in.) within a frame made of ½" × ½" square steel pipe of 16 gauge, as per approved drawings, and fixing to steel windows, doors, ventilators, etc., including cutting, welding, fixing, and all necessary accessories, excluding cost of red oxide primer and painting, complete in all respects as per specifications and Engineer’s instructions. | Per Sft | 16
12 | IRON-WORK N.S.I -35 | STEEL DOOR Providing, fabricating, and fixing steel door comprising frame made from 1" × 2" steel pipe of 16 gauge, including square pipe at lock rail and horizontal/vertical members above and below lock rail, clad with 18 SWG pressed steel sheet, complete with all necessary ironmongery (hinges, handles, lock, tower bolt, etc.), including welding, fixing, and finishing, excluding cost of red oxide primer and paint, complete in all respects as per specifications and Engineer’s instructions. | Per Sft | 28
13 | CH-10: S.no 10-15-h | CONCRETE UNDER FLOORING WHERE APPLICABLE / NEEDED (3" THICK) Laying 3" thick concrete topping (1:2:4), including compaction, surface finishing, and division into panels where required, complete in all respects. | Per Sft | 100
14 | CH-10: S.no 10-47-d | MARBLE STRIP FOR PANEL JOINTS Fixing marble strips 2" wide and 3/8" thick for dividing flooring into panels, including cutting, alignment, and finishing, complete in all respects. | Per Rft | 60
15 | ROOFING N.S.I -19 | SEALING FOR ROOF INSULATION Providing and applying crack sealing treatment using Sika® Fabric-50 and Sika Latex® SBR mixed with cement and fine aggregate slurry/mortar, applied in two coats to seal cracks, pores, and surface imperfections, complete as per manufacturer’s recommendations and the Engineer’s instructions. | Per Sft | 196
16 | NSI | STEEL GIRDER: Supply and fixing of Mild Steel I-Girder (I-Beam) of section ISMB 300 (300 mm / 12 inch), suitable for 4–5 ton lifting capacity, having standard unit weight of 44.2 kg/m (approx. 13–14 kg/ft), with a length of 14 ft, including cutting, welding, erection, provision of stiffeners (if required), bearing plates, alignment, and all necessary fittings, complete in all respects. The girder shall be manufactured from prime quality steel of approved make such as Mughal Steel, Ittefaq Steel, Amreli Steels or equivalent. | P.Nos | 1
B-Renovation of Pump Chamber (10'x10'x10') (Electrical Works)
17 | "CH-15: S.no 15-02-b-03" | PVC Conduit Pipe (1” I/D) – Recessed Wiring Providing, supplying, and installation of heavy-duty PVC conduit pipe (25mm dia), recessed in walls/slabs including cutting, chasing, fixing with approved saddles, and making good the surface, conforming to IEC 61386, complete in all respects as directed by the Engineer. | P.Rft | 27
18 | "CH-15: S.no 15-02-b-05" | PVC Conduit Pipe (1.5” I/D) – Recessed Wiring Providing, supplying, and installation of heavy-duty PVC conduit pipe (40mm dia), recessed in walls including all accessories, bends, couplers, and finishing, conforming to IEC 61386. | P.Rft | 50
19 | "CH-15: S.no 15-06-a" | Light Point Wiring (3/0.029 Cable) Providing, supplying, and installation of single-core PVC insulated and sheathed copper conductor cable (3/0.029”), 250/440V grade, from switchboard to lighting points, laid in conduit with separate wiring for each point (no looping), conforming to IEC 60227. | P.Rft | 54
20 | "CH-15: S.no 15-06-c" | Fan Wiring (7/0.029 Cable) Providing, supplying, and installation of single-core PVC insulated and sheathed copper conductor cable (7/0.029”), for ceiling fan circuits, complete as per IEC 60227. | P.Rft | 100
21 | "CH-15: S.no 15-68-f" | Wall Bracket Fan Supply and Fixing of 24" dia Direct axial Wall Bracket fan,1450Rpm, Max 50db sound level Fan shall be made with 99% purity Copper winding | P.Nos | 1
22 | ELEC N.S.I -03 | MCB (10A) Providing and installation of 10A miniature circuit breaker (MCB), 6kA breaking capacity, conforming to IEC 60898. | P.Nos | 2
23 | ELEC N.S.I -04 | MCCB (32A, TP) Providing and installation of 3-pole MCCB, 32A, 10kA breaking capacity, conforming to IEC 60947. | P.Nos | 1
24 | ELEC N.S.I -05 | MS Distribution Board (12”×12”) Providing and installation of MS DB (16-gauge), recessed type, powder-coated finish. | P.Nos | 1
25 | ELEC N.S.I -06 | PVC Bulb Holder Providing, supplying, and installation of high-quality PVC type energy saver bulb holder (batten type), suitable for LED/energy saver lamps, complete with brass contacts, heat-resistant body, and all necessary fixing accessories, wiring connections, and fittings, conforming to relevant IEC standards, complete in all respects as per specifications and as directed by the Engineer. | P.Nos | 2
26 | ELEC N.S.I -07 | LED Bulb (18W) Providing, supplying, and installation of 18W LED bulb of approved make, suitable for 220V supply, having cool daylight color temperature of 6500K, complete with standard base holder compatibility. The bulb shall be energy-efficient, with low heat emission, instant-on operation without flickering or warm-up time, and an average lifespan of not less than 25,000 hours. The product shall be eco-friendly and suitable for continuous use, complete with all necessary fittings and connections, as per specifications and as directed by the Engineer | P.Nos | 2
C-Renovationof Pump Chamber (10'x10'x10') (Plumbing Works)
27 | CH-09: S.no 09-16 | KHURAS ON ROOF (TOP) Forming a khuras on the roof of size 2' × 2' × 6", including proper shaping, finishing, and slope to facilitate drainage, complete in all respects. | Per Nos | 1
28 | CH-09: S.no 09-17 | BOTTOM KHURAS (DRAIN OUTLETS) Constructing bottom khuras in brick masonry in cement sand mortar (1:6) over 3" thick PCC (1:4:8), including proper slope, finishing, and drainage arrangement, complete in all respects. | Per Nos | 1
29 | "CH-14: S.no 14-141-b " | UPVC Pipe (4”) Rain Water Down Pipe P/L approved quality UPVC pipes for water, sewerage / Drainage supply i/c fitting, cutting, jointing, jointing material, Testing against leakage | P.Rft | 15
Grand Total Cost in PKR

## 4. MS of Renovation of Pump Hou
Backup Calculation / Detail Estimate Sheet of Pump House |  | Pump Chamber Batta Tal
Code | Activities | No | Lenght | Width | Height | Quantity | Unit
A | A-Construction of Pump Chamber (10'x10'x10') (Civil Works)
sft
1 | FLOATING COAT BEFORE PLASTER Applying a floating coat of neat cement slurry (1/32" thick) over prepared surfaces prior to plastering to enhance bond, complete in all respects.
Plaster inside
| Long Wall | 2 | 10 |  | 10 | 200
| Short Wall | 2 | 10 |  | 10 | 200
Brick in Parapet wall
| Long Wall | 2 | 11.5 |  | 2.75 | 63.25
| Short Wall | 2 | 10 |  | 2.75 | 55
|  |  |  | Total Qty |  | 518.25 | sft
2 | CEMENT PLASTER (1:3, 20MM THICK) Providing and applying cement plaster in a ratio of (1:3) 20 mm (¾") thick, on new surfaces up to a height of 20 ft, including proper surface preparation. pre-wetted to achieve a saturated surface dry (SSD) condition before application and Curing shall be carried out for a minimum period of three (3) days after application.
Plaster inside
| Long Wall | 2 | 10 |  | 10 | 200
| Short Wall | 2 | 10 |  | 10 | 200
Brick in Parapet wall
| Long Wall | 2 | 11.5 |  | 2.75 | 63.25
| Short Wall | 2 | 10 |  | 2.75 | 55
|  |  |  | Total Qty |  | 518.25 | Sft
3 | CEMENT POINTING (STRUCK JOINTS) Executing cement pointing with struck joints in cement sand mortar (1:2) on wall surfaces up to 20 ft height, including preparation and finishing, complete in all respects.
Pointing Work
| Long Wall | 2 | 11.5 |  | 10 | 230
| Short Wall | 2 | 10 |  | 10 | 200
|  |  |  | Total Qty |  | 430 | Sft
4 | PRIMER UNDER WALL PUTTY & DISTEMPER Apply a primer coat under Wall Putty & distemper on prepared surfaces, including necessary surface preparation, complete in all respects.
Plaster inside
| Long Wall | 2 | 10 |  | 10 | 200
| Short Wall | 2 | 10 |  | 10 | 200
Plaster of Roof Slab
| Roof Slab | 1 | 10 |  | 10 | 100
| Chajja | 1 | 14 |  | 2 | 28
| Chajja | 1 | 10 |  | 2 | 20
Brick in Parapet wall
| Long Wall | 2 | 11.5 |  | 2.75 | 63.25
| Short Wall | 2 | 10 |  | 2.75 | 55
Deductions
| Door | -1 | 4 |  | 7 | -28
| Window | -1 | 4 |  | 4 | -16
|  |  |  | Total Qty |  | 622.25 | sft
5 | WALL PUTTY APPLICATION Applying wall putty of 2 mm thickness over plastered surfaces to achieve a smooth and even finish, including surface preparation, complete in all respects.
Plaster inside
| Long Wall | 2 | 10 |  | 10 | 200
| Short Wall | 2 | 10 |  | 10 | 200
Plaster of Roof Slab
| Roof Slab | 1 | 10 |  | 10 | 100
| Chajja | 1 | 14 |  | 2 | 28
| Chajja | 1 | 10 |  | 2 | 20
Brick in Parapet wall
| Long Wall | 2 | 11.5 |  | 2.75 | 63.25
| Short Wall | 2 | 10 |  | 2.75 | 55
Deductions
| Door | -1 | 4 |  | 7 | -28
| Window | -1 | 4 |  | 4 | -16
|  |  |  | Total Qty |  | 622.25 | Sft
6 | RED OXIDE PRIMER Applying red oxide primer coat on prepared surfaces of steel /MS Works in the above scope of work prior to application of synthetic enamel paint of approved quality, including surface preparation and complete in all respects as per specifications and the Engineer’s instructions.
| Door | 2 | 4 |  | 7 | 56
| Window | 2 | 4 |  | 4 | 32
|  |  |  | Total Qty |  | 88 | Sft
7 | SYNTHETIC ENAMEL PAINT Providing and applying synthetic enamel paint of approved quality and specified color on new or existing surfaces of walls, doors, and windows, to achieve a uniform and even finish, complete in all respects as per specifications and Engineer’s instructions.
| Door | 2 | 4 |  | 7 | 56
| Window | 2 | 4 |  | 4 | 32
|  |  |  | Total Qty |  | 88 | Sft
8 | EMULSION PAINT(INSIDE WALLS / ROOF SLAB) – FIRST COAT Preparing surfaces and applying the first coat of emulsion paint, including surface preparation and uniform application, complete in all respects.
Plaster inside
| Long Wall | 2 | 10 |  | 10 | 200
| Short Wall | 2 | 10 |  | 10 | 200
Plaster of Roof Slab
| Roof Slab | 1 | 10 |  | 10 | 100
| Chajja | 1 | 14 |  | 2 | 28
| Chajja | 1 | 10 |  | 2 | 20
Brick in Parapet wall
| Long Wall | 2 | 11.5 |  | 2.75 | 63.25
| Short Wall | 2 | 10 |  | 2.75 | 55
Deductions
| Door | -1 | 4 |  | 7 | -28
| Window | -1 | 4 |  | 4 | -16
|  |  |  | Total Qty |  | 622.25 | Sft
9 | SNOWCEM / WEATHER SHIELD(OUT SIDE) – FIRST COAT Preparing external surfaces and applying the first coat of Snowcem/Weather Shield paint, including cleaning and surface preparation, complete in all respects.
On Pointing Work
| Long Wall | 2 | 11.5 |  | 10 | 230
| Short Wall | 2 | 10 |  | 10 | 200
|  |  |  | Total Qty |  | 430 | Sft
10 | STEEL GLAZED WINDOW WITH GLASS Fabricating, and fixing openable steel glazed window panels manufactured from L-section pipe (1½" × 1" × 18 gauge) and T-section pipe (2" × 1" × 18 gauge), including all necessary ironmongery (handles, locks, hinges, etc.), and providing, supplying, cutting, and fixing 5 mm thick plain glass, secured with approved aluminium glazing strips and sealed with silicone sealant to ensure proper fixing, airtightness, and watertightness, including all fittings, accessories, welding, cutting, handling, installation, and finishing, complete in all respects as per specifications and Engineer’s instructions.
| Window | 1 | 4 |  | 4 | 16
|  |  |  | Total Qty |  | 16 | Sft
11 | GI WIRE GAUZE FIXING (SAFETY GRILL & MOSQUITO NET) Providing, fabricating, and fixing GI wire gauze of 24 SWG (12 × 12 mesh per sq. in.) within a frame made of ½" × ½" square steel pipe of 16 gauge, as per approved drawings, and fixing to steel windows, doors, ventilators, etc., including cutting, welding, fixing, and all necessary accessories, excluding cost of red oxide primer and painting, complete in all respects as per specifications and Engineer’s instructions.
| Window | 1 | 4 |  | 4 | 16
|  |  |  | Total Qty |  | 16 | Sft
12 | STEEL DOOR Providing, fabricating, and fixing steel door comprising frame made from 1" × 2" steel pipe of 16 gauge, including square pipe at lock rail and horizontal/vertical members above and below lock rail, clad with 18 SWG pressed steel sheet, complete with all necessary ironmongery (hinges, handles, lock, tower bolt, etc.), including welding, fixing, and finishing, excluding cost of red oxide primer and paint, complete in all respects as per specifications and Engineer’s instructions.
| Door | 1 | 4 |  | 7 | 28
|  |  |  | Total Qty |  | 28 | Sft
13 | CONCRETE UNDER FLOORING WHERE APPLICABLE / NEEDED (3" THICK) Laying 3" thick concrete topping (1:2:4), including compaction, surface finishing, and division into panels where required, complete in all respects.
| Under Floor | 1 | 10 | 10 |  | 100
|  |  |  | Total Qty |  | 100 | Sft
14 | MARBLE STRIP FOR PANEL JOINTS Fixing marble strips 2" wide and 3/8" thick for dividing flooring into panels, including cutting, alignment, and finishing, complete in all respects.
| Marble strips for Flooring X-Direction | 1 | 10 |  | 3 | 30
| Marble strips for Flooring Y-Direction | 1 | 10 |  | 3 | 30
|  |  |  | Total Qty |  | 60 | Rft
15 | SEALING FOR ROOF INSULATION Providing and applying crack sealing treatment using Sika® Fabric-50 and Sika Latex® SBR mixed with cement and fine aggregate slurry/mortar, applied in two coats to seal cracks, pores, and surface imperfections, complete as per manufacturer’s recommendations and the Engineer’s instructions.
| Roof Top | 1 | 14 | 14 |  | 196
|  |  |  | Total Qty |  | 196 | Sft
16 | STEEL GIRDER: Supply and fixing of Mild Steel I-Girder (I-Beam) of section ISMB 300 (300 mm / 12 inch), suitable for 4–5 ton lifting capacity, having standard unit weight of 44.2 kg/m (approx. 13–14 kg/ft), with a length of 14 ft, including cutting, welding, erection, provision of stiffeners (if required), bearing plates, alignment, and all necessary fittings, complete in all respects. The girder shall be manufactured from prime quality steel of approved make such as Mughal Steel, Ittefaq Steel, Amreli Steels or equivalent.
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
B | B-Construction of Pump Chamber (10'x10'x10') (Electrical Works)
17 | PVC Conduit Pipe (1” I/D) – Recessed Wiring Providing, supplying, and installation of heavy-duty PVC conduit pipe (25mm dia), recessed in walls/slabs including cutting, chasing, fixing with approved saddles, and making good the surface, conforming to IEC 61386, complete in all respects as directed by the Engineer.
|  | 1 | 27 |  |  | 27
|  |  |  | Total Qty |  | 27 | RFt
18 | PVC Conduit Pipe (1.5” I/D) – Recessed Wiring Providing, supplying, and installation of heavy-duty PVC conduit pipe (40mm dia), recessed in walls including all accessories, bends, couplers, and finishing, conforming to IEC 61386.
|  | 1 | 50 |  |  | 50
|  |  |  | Total Qty |  | 50 | Rft
19 | Light Point Wiring (3/0.029 Cable) Providing, supplying, and installation of single-core PVC insulated and sheathed copper conductor cable (3/0.029”), 250/440V grade, from switchboard to lighting points, laid in conduit with separate wiring for each point (no looping), conforming to IEC 60227.
|  | 1 | 54 |  |  | 54
|  |  |  | Total Qty |  | 54 | Rft
20 | Main & Sub Main Wiring (7/0.029 Cable) Providing, supplying, and installation of single-core PVC insulated and sheathed copper conductor cable (7/0.029”), for ceiling fan circuits, complete as per IEC 60227.
|  | 1 | 100 |  |  | 100
|  |  |  | Total Qty |  | 100 | Rft
21 | Wall Bracket Fan Supply and Fixing of 24" dia Direct axial Wall Bracket fan,1450Rpm, Max 50db sound level Fan shall be made with 99% purity Copper winding
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
22 | MCB (10A) Providing and installation of 10A miniature circuit breaker (MCB), 6kA breaking capacity, conforming to IEC 60898.
|  | 2 |  |  |  | 2
|  |  |  | Total Qty |  | 2 | No.
23 | MCCB (32A, TP) Providing and installation of 3-pole MCCB, 32A, 10kA breaking capacity, conforming to IEC 60947.
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
24 | MS Distribution Board (12”×12”) Providing and installation of MS DB (16-gauge), recessed type, powder-coated finish.
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
25 | PVC Bulb Holder Providing, supplying, and installation of high-quality PVC type energy saver bulb holder (batten type), suitable for LED/energy saver lamps, complete with brass contacts, heat-resistant body, and all necessary fixing accessories, wiring connections, and fittings, conforming to relevant IEC standards, complete in all respects as per specifications and as directed by the Engineer.
|  | 2 |  |  |  | 2
|  |  |  | Total Qty |  | 2 | No.
26 | LED Bulb (18W) Providing, supplying, and installation of 18W LED bulb of approved make, suitable for 220V supply, having cool daylight color temperature of 6500K, complete with standard base holder compatibility. The bulb shall be energy-efficient, with low heat emission, instant-on operation without flickering or warm-up time, and an average lifespan of not less than 25,000 hours. The product shall be eco-friendly and suitable for continuous use, complete with all necessary fittings and connections, as per specifications and as directed by the Engineer
|  | 2 |  |  |  | 2
|  |  |  | Total Qty |  | 2 | No.
C | C-Construction of Pump Chamber (10'x10'x10') (Plumbinf Works)
27 | KHURAS ON ROOF (TOP) Forming a khuras on the roof of size 2' × 2' × 6", including proper shaping, finishing, and slope to facilitate drainage, complete in all respects.
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
28 | BOTTOM KHURAS (DRAIN OUTLETS) Constructing bottom khuras in brick masonry in cement sand mortar (1:6) over 3" thick PCC (1:4:8), including proper slope, finishing, and drainage arrangement, complete in all respects.
|  | 1 |  |  |  | 1
|  |  |  | Total Qty |  | 1 | No.
29 | UPVC Pipe (4”) Rain Water Down Pipe P/L approved quality UPVC pipes for water, sewerage / Drainage supply i/c fitting, cutting, jointing, jointing material, Testing against leakage
|  | 15 |  |  |  | 15
|  |  |  | Total Qty |  | 15 | Rft