## Summary Sheet
Boring and Installation of a submersible pump for domestic water use at Faqeerabad
Abstract Of Cost
S.NO. | Description | No's | Total Amount
1 | Boring and Installation of a submersible pump for domestic water use | 1 | 0
2 | Water Supply Network | 1 | 0
3 | Solar | 1 | 0
| TOTAL COST Rs. |  | 0
| TOTAL COST Rs. (M) |  | 0

## BOQ- Pump
Boring and Installation of a submersible pump for domestic water use at Faqeerabad
S.No | Description | Unit | Quantity | Unit Rate | Total Amount
Boring and Installation of a submersible Pump having a depth of (600 feet) at Faqeerabad (one pump for main Road Side & one pump for one Leather Goudam)
1 | Providing all labor, plant, equipment, tools, and machinery for rotary drilling/boring in all types of water-bearing strata up to a depth of 600 ft(2 bores) below ground level, with a borehole diameter of 300 mm (12 inches), including drilling fluid, removal of cuttings, borehole cleaning, and all incidental works required for complete execution, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | Rft | 1200
2 | uPVC casing pipe Providing, installing, jointing, and testing of 8-inch internal diameter casing pipe (350 ft length) for bore installation, complete in all respects including rubber seals/packing, non-return (check) valve of 8-inch diameter, clamps, and all necessary fittings, accessories, and appurtenances, including all contractual obligations and unforeseen items as required for proper completion of the work. | Rft | 700
3 | uPVC casing filter pipe Providing, installing, jointing, and testing of 8-inch internal diameter casing filter pipe (250 ft length) for bore installation, complete in all respects including rubber seals/packing, non-return (check) valve of 8-inch diameter, clamps, and all necessary fittings, accessories, and appurtenances, including all contractual obligations and unforeseen items as required for proper completion of the work. | Rft | 500
4 | Providing, supplying, and placing graded pea gravel shrouding in the annular space between the borehole wall and the blind pipe/strainer, including loading, transportation, placement, and compaction as required, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | Rft | 1200
5 | Providing, supplying, installing, testing, and commissioning of a 5.5 HP submersible pump with 100% copper winding, permanent magnet brushless (BLDC) motor, manufactured by an ISO-certified company, maximum total dynamic head of 167 m, suitable for operation at an ambient temperature of up to 50°C, including controller, cable joints, safety rope, non-return valve, clamps, connectors, and all other necessary fittings and accessories required for complete installation and satisfactory operation, in accordance with the manufacturer's recommendations and the Engineer's approval, complete in all respects. | No. | 2
6 | Providing, supplying, and laying 110/0.76 full-gauge copper submersible pump cable, including all necessary connections, jointing, termination, testing, commissioning, and all incidental works required for complete installation, in accordance with the approved drawings and specifications, complete in all respects. | Rft | 1400
7 | Providing, supplying, and installing PVC-coated stainless steel (SS) suspension rope for lowering and supporting the submersible pump inside the borehole, including all necessary clamps, thimbles, shackles, fasteners, fixing accessories, testing, and all incidental works required for complete installation, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | Rft | 1240
8 | Providing all labor, equipment, machinery, transportation, loading, hauling, unloading, and safe disposal of surplus drilling sludge, mud, cuttings, and other waste materials generated during borehole drilling at an approved disposal site, including site cleaning and restoration, in accordance with the Engineer's instructions and applicable environmental requirements, complete in all respects. | Trip | 70
9 | Supply and installation of a project signboard fabricated from stainless steel (SS) sheet, nominal size 24″ × 24″, or as directed by the Engineer-in-Charge, complete in all respects. The work shall include cutting, fabrication, fixing, anchoring, and finishing of the signboard, including all necessary materials, fasteners, tools, labor, and safety measures, in accordance with the drawings and technical specifications. | No. | 2
Sub Total - A
Water Sampling and Laboratory Testing
10 | Collection and submission of a minimum of two water samples from each borehole to an approved laboratory for physical, chemical, and bacteriological analysis, including proper handling, labeling, and submission of certified test reports. | 2 Set | 2
Sub Total - B
Total Cost
17 | Provisional Sums | LS
Grand Total cost in PKR

## BOQ-Water Supply
Water Supply Network for Domestic Use at Faqeerabad
S.No | Description | Unit | Quantity | Unit Rate | Total Amount
1 | Excavation for pipe line in trenches, and pits in hard soils i/c trimming and dressing sides to true alignment and shape levelling of beds of trenches to correct level and grade, cutting , joint holes and disposal of surplus earth within a one chain as directed by Engineer Incharge . Providing fence guards, lights, flags and temporary crossings for non-vehicular traffic where ever required lift upto 5 ft. (1.52m) and lead upto one chain (30.5m). | Cft | 3200
2 | Refilling the excavated stuff in trenches 6" thick layer i/c watering ramming to full compaction etc. complete in all respect. | Cft | 3200
3 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects except excavation. (32 mm dia ) PN-10 , 1. 25" dia | Rft | 4400
4 | Providing Chamber 3'x2'(915x615 mm) inside diamension 41/2'(1372 mm)deep as per approved design for sluice value 3"to12"dia with 18" (457mm)dia inside cost iron cover and frame(wt=1 cwt 3qr) fixed in RCC 1:2:4 (102mm)thick (with 5 Lbs steel per cft) 9"(299mm) thick burnt brick masonary wall setin 1:6 cement mortar 6"(1152mm) thick cement concrete 1:3:6 in foundation 1"(25mm)thick cement concrete 1:3:6 in foundation 1"(25mm) thick cement concrete1:2:4 flooring 1/2" (12.5mm) thick cement plaster 1:3 to all inside wall surface and to top i/c providing and fixing M.S foot rest at everyone foot beyond 21/2ft depth curing, excavation, back filling and disposal of surplus earth etc. complete in all respect. | Each | 4
5 | Provision and installation of Street connections, including all necessary accessories such as connection clamps, ball valves, and associated fittings, complete in all respects.The work shall be carried out in accordance with the drawings, technical specifications, site conditions, and as directed by the Engineer-in-Charge. | Each | 40
Total Cost
6 | Provisional Sums | LS
Grand Total cost in PKR

## BOQ -Solar
Supply, Installation & Commissioning of 5. 5HP submersible Pump in Boring (One pump for main road side & one pump for Leather Goudam) (Solar Powered)
S.No. | Description | Unit | Quantity | Unit Rate | Total Amount
1 | Providing, supplying, and fixing 585 W double-glass monocrystalline solar photovoltaic (PV) panels of Jinko, Longi, or an approved equivalent make, including manufacturer's standard warranty, and complete installation in all respects as per the approved drawings and specifications. | Watt | 16380
2 | Providing, fabricating, supplying, and fixing L2-type galvanized steel solar panel mounting stands fabricated from 14-gauge material, including all necessary nuts, bolts, washers, anchor fasteners, brackets, touch-up paint, and all other accessories required for complete installation, in accordance with the approved drawings and specifications, complete in all respects. | No. | 14
3 | Protection, Control and Monitoring Components for 8 kW Solar VFD Supply, installation, testing, and commissioning of complete protection, control, and monitoring system for 8 kW solar pump VFD, including MC4 connectors; 4th generation 3-in-1 voltage protection device with integrated kWh meter (or equivalent approved); 4-pole AC circuit breakers for utility (k electric) input, light load, and heavy load circuits; changeover switch/breaker ; double-pole DC circuit breaker for PV string(s); AC and DC surge protection devices; including all interconnections, terminations, mounting, and accessories, complete in all respects as per approved specifications and as directed by the Engineer. | No. | 2
4 | Providing, laying, testing, and commissioning of 6 mm, 2-core DC flexible cable of Fast, GM, Newage (Pakistan), or an approved equivalent make, complete in all respects as per the Engineer's instructions and technical specifications. | Rft | 140
5 | Providing, laying, testing, and commissioning of 10 mm, 2-core AC flexible cable of Fast, GM, Newage (Pakistan), or an approved equivalent make, complete in all respects as per the Engineer's instructions and technical specifications. | Rft | 90
6 | Providing and fixing all hardware, conduits, connectors, fittings, accessories etc. essential for solar system and complete in all respect. | Job | 2
7 | Providing transportation, loading, unloading, handling, and safe delivery of solar photovoltaic (PV) panels, inverter(s), mounting structure, cables, accessories, and all associated materials from the supplier's premises to the project site, complete in all respects. | LS | 2
8 | Earthing System for Inverter and Steel Structure Supply, installation, testing, and commissioning of a complete earthing system for inverter and solar mounting steel structure, comprising independent earthing points for each system, with a minimum spacing of 8 ft between earth pits, complete in all respects as per specifications and as directed by the Engineer.Each earthing point shall consist of a bore of minimum 10 ft depth and 3" diameter, incorporating a 2" diameter GI pipe installed vertically. A 16 mm diameter copper rod shall be inserted inside the GI pipe, surrounded by layers of charcoal and salt to enhance conductivity. The copper rod shall be connected using 12-gauge copper wire with appropriate copper U-clamps. The earthing conductors shall be routed separately, with independent connections provided to the solar steel mounting structure and the inverter, ensuring effective grounding and system protection.All materials, installation, and workmanship shall conform to approved specifications or as per the Engineer instruction. | Job | 2
Total Cost
9 | Provisional Sums
Grand Total Cost (PKR)

## MS- Pump
Boring and Installation of a submersible pump for domestic water use at Faqeerabad
Measurement Sheet
S.No | Description | No. | Unit | Length | Width | Height | Total Quantity
Boring and Installation of a submersible Pump having a depth of (600 feet) at Faqeerabad (one pump for main Road Side & one pump for one Leather Goudam)
1 | Providing all labor, plant, equipment, tools, and machinery for rotary drilling/boring in all types of water-bearing strata up to a depth of 600 ft (2 bores) below ground level, with a borehole diameter of 300 mm (12 inches), including drilling fluid, removal of cuttings, borehole cleaning, and all incidental works required for complete execution, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | 2 | Rft | 600 |  |  | 1200
2 | uPVC casing pipe Providing, installing, jointing, and testing of 8-inch internal diameter casing pipe (350 ft length) for bore installation, complete in all respects including rubber seals/packing, non-return (check) valve of 8-inch diameter, clamps, and all necessary fittings, accessories, and appurtenances, including all contractual obligations and unforeseen items as required for proper completion of the work. | 2 | Rft | 350 |  |  | 700
3 | uPVC casing filter pipe Providing, installing, jointing, and testing of 8-inch internal diameter casing filter pipe (250 ft length) for bore installation, complete in all respects including rubber seals/packing, non-return (check) valve of 8-inch diameter, clamps, and all necessary fittings, accessories, and appurtenances, including all contractual obligations and unforeseen items as required for proper completion of the work. | 2 | Rft | 250 |  |  | 500
4 | Providing, supplying, and placing graded pea gravel shrouding in the annular space between the borehole wall and the blind pipe/strainer, including loading, transportation, placement, and compaction as required, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | 2 | Rft | 600 |  |  | 1200
5 | Providing, supplying, installing, testing, and commissioning of a 5.5 HP submersible pump with 100% copper winding, permanent magnet brushless (BLDC) motor, manufactured by an ISO-certified company, maximum total dynamic head of 167 m, suitable for operation at an ambient temperature of up to 50°C, including controller, cable joints, safety rope, non-return valve, clamps, connectors, and all other necessary fittings and accessories required for complete installation and satisfactory operation, in accordance with the manufacturer's recommendations and the Engineer's approval, complete in all respects. | 2 | No. | 1 |  |  | 2
6 | Providing, supplying, and laying 110/0.76 full-gauge copper submersible pump cable, including all necessary connections, jointing, termination, testing, commissioning, and all incidental works required for complete installation, in accordance with the approved drawings and specifications, complete in all respects. | 2 | Rft | 700 |  |  | 1400
7 | Providing, supplying, and installing PVC-coated stainless steel (SS) suspension rope for lowering and supporting the submersible pump inside the borehole, including all necessary clamps, thimbles, shackles, fasteners, fixing accessories, testing, and all incidental works required for complete installation, in accordance with the approved specifications and the Engineer's instructions, complete in all respects. | 2 | Rft | 620 |  |  | 1240
8 | Providing all labor, equipment, machinery, transportation, loading, hauling, unloading, and safe disposal of surplus drilling sludge, mud, cuttings, and other waste materials generated during borehole drilling at an approved disposal site, including site cleaning and restoration, in accordance with the Engineer's instructions and applicable environmental requirements, complete in all respects. | 2 | Trip | 35 |  |  | 70
9 | Supply and installation of a project signboard fabricated from stainless steel (SS) sheet, nominal size 24″ × 24″, or as directed by the Engineer-in-Charge, complete in all respects. The work shall include cutting, fabrication, fixing, anchoring, and finishing of the signboard, including all necessary materials, fasteners, tools, labor, and safety measures, in accordance with the drawings and technical specifications. | 2 | No. | 1 |  |  | 2
10 | Collection and submission of a minimum of two water samples from each borehole to an approved laboratory for physical, chemical, and bacteriological analysis, including proper handling, labeling, and submission of certified test reports. | 2 | 2 Set | 1 |  |  | 2

## MS-Water Supply
Water Supply Network for Domestic Use at Faqeerabad
Measurement Sheet
S.No | Description | No. | Unit | Length | Width | Height | Total Quantity
1 | Excavation for pipe line in trenches, and pits in hard soils i/c trimming and dressing sides to true alignment and shape levelling of beds of trenches to correct level and grade, cutting , joint holes and disposal of surplus earth within a one chain as directed by Engineer Incharge . Providing fence guards, lights, flags and temporary crossings for non-vehicular traffic where ever required lift upto 5 ft. (1.52m) and lead upto one chain (30.5m). | 2 | Cft | 1600 | 1 | 1 | 3200
2 | Refilling the excavated stuff in trenches 6" thick layer i/c watering ramming to full compaction etc. complete in all respect. | 2 | Cft | 1600 | 1 | 1 | 3200
3 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects except excavation. (32 mm dia ) PN-10 , 1. 25" dia | 2 | Rft | 2200 |  |  | 4400
4 | Providing Chamber 3'x2'(915x615 mm) inside diamension 41/2'(1372 mm)deep as per approved design for sluice value 3"to12"dia with 18" (457mm)dia inside cost iron cover and frame(wt=1 cwt 3qr) fixed in RCC 1:2:4 (102mm)thick (with 5 Lbs steel per cft) 9"(299mm) thick burnt brick masonary wall setin 1:6 cement mortar 6"(1152mm) thick cement concrete 1:3:6 in foundation 1"(25mm)thick cement concrete 1:3:6 in foundation 1"(25mm) thick cement concrete1:2:4 flooring 1/2" (12.5mm) thick cement plaster 1:3 to all inside wall surface and to top i/c providing and fixing M.S foot rest at everyone foot beyond 21/2ft depth curing, excavation, back filling and disposal of surplus earth etc. complete in all respect. | 2 | Each | 2 |  |  | 4
5 | Provision and installation of Street connections, including all necessary accessories such as connection clamps, ball valves, and associated fittings, complete in all respects.The work shall be carried out in accordance with the drawings, technical specifications, site conditions, and as directed by the Engineer-in-Charge. | 2 | Each | 20 |  |  | 40

## MS-Solar
Supply, Installation & Commissioning of 5. 5HP submersible Pump in Boring (One pump for main road side & one pump for Leather Goudam) (Solar Powered)
Measurement Sheet
S.No. | Description | No. | Unit | Length | Width | Height | Total Quantity
1 | Providing, supplying, and fixing 585 W double-glass monocrystalline solar photovoltaic (PV) panels of Jinko, Longi, or an approved equivalent make, including manufacturer's standard warranty, and complete installation in all respects as per the approved drawings and specifications. | 2 | Watt | 8190 |  |  | 16380
2 | Providing, fabricating, supplying, and fixing L2-type galvanized steel solar panel mounting stands fabricated from 14-gauge material, including all necessary nuts, bolts, washers, anchor fasteners, brackets, touch-up paint, and all other accessories required for complete installation, in accordance with the approved drawings and specifications, complete in all respects. | 2 | No. | 7 |  |  | 14
3 | Protection, Control and Monitoring Components for 8 kW Solar VFD Supply, installation, testing, and commissioning of complete protection, control, and monitoring system for 8 kW solar pump VFD, including MC4 connectors; 4th generation 3-in-1 voltage protection device with integrated kWh meter (or equivalent approved); 4-pole AC circuit breakers for utility (k electric) input, light load, and heavy load circuits; changeover switch/breaker ; double-pole DC circuit breaker for PV string(s); AC and DC surge protection devices; including all interconnections, terminations, mounting, and accessories, complete in all respects as per approved specifications and as directed by the Engineer. | 2 | No. | 1 |  |  | 2
4 | Providing, laying, testing, and commissioning of 6 mm, 2-core DC flexible cable of Fast, GM, Newage (Pakistan), or an approved equivalent make, complete in all respects as per the Engineer's instructions and technical specifications. | 2 | Rft | 70 |  |  | 140
5 | Providing, laying, testing, and commissioning of 10 mm, 2-core AC flexible cable of Fast, GM, Newage (Pakistan), or an approved equivalent make, complete in all respects as per the Engineer's instructions and technical specifications. | 2 | Rft | 45 |  |  | 90
6 | Providing and fixing all hardware, conduits, connectors, fittings, accessories etc. essential for solar system and complete in all respect. | 2 | Job | 1 |  |  | 2
7 | Providing transportation, loading, unloading, handling, and safe delivery of solar photovoltaic (PV) panels, inverter(s), mounting structure, cables, accessories, and all associated materials from the supplier's premises to the project site, complete in all respects. | 2 | LS | 1 |  |  | 2
8 | Earthing System for Inverter and Steel Structure Supply, installation, testing, and commissioning of a complete earthing system for inverter and solar mounting steel structure, comprising independent earthing points for each system, with a minimum spacing of 8 ft between earth pits, complete in all respects as per specifications and as directed by the Engineer.Each earthing point shall consist of a bore of minimum 10 ft depth and 3" diameter, incorporating a 2" diameter GI pipe installed vertically. A 16 mm diameter copper rod shall be inserted inside the GI pipe, surrounded by layers of charcoal and salt to enhance conductivity. The copper rod shall be connected using 12-gauge copper wire with appropriate copper U-clamps. The earthing conductors shall be routed separately, with independent connections provided to the solar steel mounting structure and the inverter, ensuring effective grounding and system protection.All materials, installation, and workmanship shall conform to approved specifications or as per the Engineer instruction. | 2 | Job | 1 |  |  | 2